SWP 32 - Procedure for the removal of redundant, underground, copper (decommissioned) LP Gas Pipes

| Who: | Paneltec Gas Operations Team – Operative with Cert II or III in Gas Industry Operations, and or appropriately trained and experienced Construction Worker L2 with Gas Test Atmospheres Accreditation. |
| --- | --- |
| When: | On receipt of a Work Order and or Work Request |
| Why: | To ensure a common standard is applied when removing redundant, underground, copper (decommissioned) LP gas pipes. |
| You Need: | - To ensure with the customer that the gas installation has been previously decommissioned by a licensed gasfitter and the appropriate notice has been submitted to the Director of Gas Safety. Also, obtain written confirmation from the customer that they are not and will never be using the redundant pipe again for the conveyance of a fuel gas, liquid(s) or as any type of conduit. - Shifters 10”, 12” & 14” - B Press Crimp Tool & Heads - B press Cap end Gas Fittings (DN to suit pipe size) - Pipe Tubing Cutters - Steel wool - Appropriately calibrated 4 gas alarm - Personal Protective Equipment (PPE) - Half face respirator fitted with organic/inorganic vapors (6057 Cartridges) - Dry chemical fire extinguisher |
| NOTE: | *Do not remove the gas pipe if confirmation from the customer has not been received of the gas installations decommissioning by a licensed gasfitter. *Do not remove any component of the redundant pipe if the pipe is still connected to a gas installation and or a gas storage system. |

1.	PIPE SECTION REMOVAL

| Step No. | Task Description | Reference |
| --- | --- | --- |
| 1.0 | Check the 4-gas alarm is calibrated and the battery level will be sufficient for the duration of the works. Clip the gas alarm to the hip of the operative for the duration of the works. If at any stage the alarm sounds pull back to the designated emergency assembly point (upwind of site) and call the customer representative and or Paneltec management. |  |
| 1.1 | Ensure the pipe to be removed is free from nitrogen, pressure, gas and or ground water by untightening an above ground redundant cap/fitting. All PPE shall be worn in accordance with Paneltec’s Pipe Policy. Half faced respirator and cartridges shall be used if the pipe diameter is larger than 20mm. |  |
| 1.2 | Once it has been confirmed the pipe is free of pressure, gas and or ground water the pipe section removal process can begin. Have a dry chemical fire extinguisher beside the excavation site. |  |
| 1.3 | Excavate down to the depth of the redundant pipe with vacuum truck or hand tools (Use Vacuum Truck SWMS if this is the preferred method) and clear away a space sufficient for application of the copper pipe tubing cutters around the pipe. Ensure the excavation exit is free and unrestricted, use ladder if and where required. |  |
| 1.4 | Adorn the half-faced respirator and all PPE in accordance with our PIPE Policy, mark the required removal section of the pipe and clean the pipe within 100mm either side of the proposed cut/capped line with steel wool. |  |
| 1.5 | Fit the pipe tubing cutters to the copper pipe and proceed to cut the pipe. |  |
| 1.6 | If gas alarm sounds, and or ground water or pressure is noted when the cutting wheel cuts through the pipe, evacuate the excavation immediately and assemble at the emergency assembly point. (Upwind of site) and call the customer representative and or Paneltec Management. |  |
| 1.7 | Once it has been safely determined the excavation and pipe are free of gas, pressure and ground water. The pipe ends can be cleaned again with steel wool. |  |
| 1.8 | Prepare the B Press crimping tool and head, fit cap ends to pipe and crimp in position |  |
| 1.9 | Repeat section 1.3 – 1.9 for the other end of the pipe if and where required. |  |

- PIPE SECTION REMOVAL DRAWING

| 2.0 | Advise customer representative of the completed works and ask them to amend any on-site drawings they have of the section of redundant pipe being removed, where applicable. |  |
| --- | --- | --- |

- PIPE SECTION DISPOSAL

| 3.0 | Advise customer of their responsibility to dispose of the section of copper pipe and take to an approved waste disposal centre. |  |
| --- | --- | --- |