## OBJECTIVE

This document describes the preparation and welding procedures for safe and efficient work practices when using electro-fusion welding equipment.

## HAZARD MANAGEMENT

| Hazard management |  |  |  |
| --- | --- | --- | --- |
|  | Manual handling | Lifting pipes and bending | Follow safe manual handling procedures |
|  | Hot | Hot welding equipment | Wear appropriate P.P.E when required |

## WELDING PROCEDURE

### Prepare pipe for welding

    - Use rotary scraper to scrape end of pipe :

    - Fit end of pipe into rotary scraper – photo 1

    - Tighten scraper and adjust to required setting – photos 1 & 2

    - Turn handle of rotary scraper until scraped area is clear of length required for specific joiner (check inside joiner to determine appropriate length) – photos 3 & 4

    - Use handheld scraper:

- Hold pipe firmly – photo 5

- Mark pipe with white marker – photo 6

- Scrape manual scraper toward end of pipe until no sign of white marker remains and scraped area is clear of length required for specific joiner – photos 7 & 8

    - Scrape any ‘dags’ from end of pipe if necessary – photo 8

| Photos 1 & 2: Fit pipe into rotary scraper and adjust Photo 3: Turn handle to scrape |  |  |
| --- | --- | --- |

| Photo 4: Pipe scraped with rotary scraper Photo 5: Manual scraper Photo 6: Mark with white marker |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Photos 7 & 8: Scrape toward end of pipe and remove ‘dags’ Photos 9 & 10: Clean end of pipes and fit joiner |  |  |  |  |  |
| Check all sign of white marker are removed |  |  |  |  |  |

    - Clean inside and outside end of pipe with alcohol wipes to ensure all dirt is removed, ensuring that final wipe is directed toward end of pipe – photo 9

    - Fit appropriate joiner to both ends of pipe, ensuring fitting is very straight on pipes and secure – photo 10

    - Mark each side of joiner with white marker (to check it doesn’t move during welding)

### Welding Pipes

    - Attach welder fittings to joiner – photos 11, 12, 13, 14 & 15

NOTE: Fitting may have to be colour coded to joiner depending on type of joiner used

    - Plug welder into generator – photo 16

    - Turn generator on – photo 16

    - Check weld times and temperature on joiner packet – photo 17

    - Use arrows on welder console to manually adjust time and temperature – photo 18

    - Follow instructions on console screen to push green button three (3) times – photos 18 & 19

    - Screen will count down weld time and indicate process is complete, by displaying “OK” – photo 19

    - Wait for appropriate cooling time, before checking weld or removing fittings (check joiner packet).

| Photo 11, 12 & 13: One type of joiner and fittings (not colour coded) |  |  |
| --- | --- | --- |
| Photos 14 & 15: Colour coded joiner and fittings Photo 16: Generator |  |  |
| Red Black |  |  |

| Photo 17: Check time and temp Photos 18 & 19: Welder console and screen on packaging Green button Arrows “OK” |  |  |
| --- | --- | --- |

    - Check white lines to ensure joiner did not move during weld time – photo 20

    - Turn welder off

    - Remove fittings from joiner

    - Check indicator nipples have risen to confirm successful weld (where appropriate) – photo 20

    - Turn generator off

    - Unplug welder from generator and pack up

    - Record relevant information on pipe with permanent marker – photo 21:

- Time weld was completed

- Date

- Initials of person responsible for weld (or persons individual number as required for service such as TasGas)

| Photo 20: Check white lines and indicator nipples | Photo 21: Write relevant information in permanent marker |
| --- | --- |