| Project: |  |
| --- | --- |
| ITP No.: |  |
| ITP Title |  |
| ITP Date |  |

THIS INSPECTION & TEST PLAN (ITP) INCLUDES THE FOLLOWING DOCUMENTS AND IS APPROVED FOR USE:

| PART 1 |  |
| --- | --- |
| PART 2 |  |
| PART 3 |  |
| APPENDICES |  |

| CUSTOMER REFERENCE NO. |  |
| --- | --- |

PROJECT SPECIFICATIONS & REFERENCE DOCUMENTS:

| 1): AS/NZS 2033: 2008 Installation of polyethylene pipe systems | 5): ISO 9001 Quality Assurance |
| --- | --- |
| 2): AS/NZS 2566.2: 2002 Buried flexible pipelines part 2: Installation | 6): ISO 13953 Polyethylene (PE) pipes and fittings |
| 3): AS/NZS 4130:2009 Polyethylene (PE) pipe for pressure applications | 7): (PIPA) technical guidelines and information |
| 4): AS/NZS 2885.1:2018 (series) Pipelines - Gas and liquid petroleum Design and construction | 8): |

| DOCUMENT HISTORY | NAME & POSITION | SIGNATURE | DATE |
| --- | --- | --- | --- |
| Prepared by: |  |  |  |
| Approved by: |  |  |  |
| Paneltec Acceptance: |  |  |  |
| Designer/Customer Acceptance: (If Applicable ) |  |  |  |

| Customer Name (if applicable) |  | Work Pack No: |  | ITP No: |  |
| --- | --- | --- | --- | --- | --- |
| Customer Responsible Engineer: |  | Customer Supervisor: (if applicable) |  | Date Opened: | / / 2021 |
| Paneltec Project Manager: |  | Paneltec Supervisor: |  | Supervisors PH No: |  |
| Customer Lot Number: |  | Customer Lot Description: |  |  |  |

PROJECT DETAILS:

|  |  |  |  |  |  |  | CONSTRUCTION VERIFICATION (Initial and Date) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item No. | Inspection / Test Point | Responsibility | Specification Reference | Conformance Criteria | Method | Frequency | Contractor | Designer / IV / Client Rep. | Customer | Records or Checklist Reference |
| Preliminaries |  |  |  |  |  |  |  |  |  |  |
| 1. | Welding Prequalification Documents | CR | WSAA 01-2004-3.1 WSAA 03 – 2011-3.1 | [PROJECT HOLD POINT] Contractor must complete and supply all prequalification documentation including: - Welding operator qualified to perform works Welding Machine within calibration and a sample weld recently subjected to destructive testing at a NATA accredited facility in accordance with ISO 13954 | R | Prior to commencing works | V | - | HP | Welder qualified by an RTO and certificate available. |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 2. | Supply of Pipe & Fittings | CR, | WSAA 03 – 2011-3.1 Cl12.1 Cl12.3.4 AS 2280 TWP-19-074-001 General Notes | [PROJECT HOLD POINT] - Use only products and materials authorised by TasWater, in accordance with the Technical Specification or supplied by TasWater. - Products and materials to be submitted for approval - All HDPE pipe and fittings to be PE100, PE63 pressure rating PN16. - Reject any non-conforming materials. - Ensure delivered products and materials are fit for use. - Ensure pipes are compliant with WSAA Code requirements. | I,R | Inspection when receiving pipe & fittings | V |  | HP | QC Inspection Pipe and fittings material certificates |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 3. | Supply of backing flanges, bolts, nuts and gaskets | CR, SE | AS4087 Metallic flanges for waterworks purposes Table 3.1 AS4331. Table 11 WSA 109-2011 Flange Gaskets and O-Rings, MWRA-W-306A & 306B, WSA PS 312 for DICL gaskets | [PROJECT HOLD POINT] - Use only products and materials authorised by TasWater CDO, in accordance with the Technical Specification or supplied by TasWater. - Reject any non-conforming materials. - Ensure delivered products and materials are fit for use. - Stainless steel backing ring material to be ASTM A240M - Stainless steel backing rings are rated to PN16 - Nominated grade of 316 bolt or studs - Nominated gasket material for both PE & DICL flange joints | I, r | Inspection when receiving | V |  | HP | QC Inspection Material certificates |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 4. | Supply of valves, Valve covers | CR, SE | WSAA 03 2011-3.1 CL8 Taswater supplement WSA 03 2011-3.1 CL8 TWP-19-074-001 General notes MWRA-W-301 | [PROJECT HOLD POINT] - Use only products and materials authorised by TasWater CDO, in accordance with the Technical Specification or supplied by TasWater. - Flange gate valves in accordance with WSAA 03 2011 3.1 - Valves to be clockwise closing, resilient seated epoxy coated, a minimum of PN16 pressure rating. - Surface fittings as per MWRA-W-302 | I,R | Prior to installation and Inspection when receiving into Paneltec Depot | V |  | HP | QC Inspection Valve Data Sheet |

|  |  |  |  |  |  |  | CONSTRUCTION VERIFICATION (Initial and Date) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item No. | Inspection / Test Point | Responsibility | Specification Reference | Conformance Criteria | Method | Frequency | Contractor | Designer / IV / Client Rep. | Customer | Records or Checklist Reference |
| 5. | Nomination of trench and back fill material | CR | WSAA 03 2011-3.1 CL 16 Taswater supplement WSA 03 2011-3.1 CL 17 TWP-19-074-001, MWRA standard drawings | [PROJECT HOLD POINT] - All imported materials/components to be submitted and approved by TasWater | R |  | HP |  | HP | Van Diemen Quarry Records |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 6. | Light Duty Asphalt Pavements | CR | TW-19-074-0001 Typical Trench details, LGAT TSD-R09 v1 | - Light Duty Asphalt Pavement designed to AC7 - Min 35 mm thick | R | Prior to re-instatement of road, Pavement | V |  | V | Asphalt Design |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 7. | Marker Tape Supply | CR | TWP-19-074-001 | ELECTROMAGNETIC METAL IMPREGNATED MARKER TYPE | R | Inspection at delivery to Paneltec Depot | V |  | V | Prior to use and backfill |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 8. | Water Quality Test | S | MWRA specification 04-02-2.0 | Results from the water quality sample meeting the requirements of the Water Quality Compliance Specification 04-02-2.0 | T | Prior to cutover of property service connections | HP | - | V | Test Certificate |
| 9. | Community and Stakeholder engagement | S |  | [PROJECT HOLD POINT] TasWater Service Delivery and Community engagement team notified of works | R | At least 10 days prior to construction commencement | V |  | V |  |

|  |  |  |  |  |  |  | CONSTRUCTION VERIFICATION (Initial and Date) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item No. | Inspection / Test Point | Responsibility | Specification Reference | Conformance Criteria | Method | Frequency | Contractor | Designer / IV / Client Rep. | Customer | Records or Checklist Reference |
| Construction (In-process) Inspections and Tests |  |  |  |  |  |  |  |  |  |  |
| 9. | Horizontal Directional Drilling | CR | WSAA 3 2011-3.1 CL13.13. MWRA-W-213, TW-19-074-001 General Notes TW-19-074-0001 Typical Trench details | [ PROJECT HOLD POINT] - Geotechnical ground conditions assessed as suitable for HDD - Excavation permit is signed and authorised. - Correct depth of cover achieved, trace wire used. - Bore logs submitted. - Bore holes cleaned by reaming or other approved method. - Entry and exit holes meet open cut trenching standards. | I | Daily | WP |  | V | Checklists, Bore logs, Photos |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 11. | Electrofusion welding | CR | WSAA 03 2011 3.1 CL MWRA 15.21.3, MS Civil SOP MSP045 | - Cut pipe ends dead square and debur. - Use a restraint, ovality and alignment tool to hold all pipelines and fittings in position as the weld is undertaken. - Apply witness marks at the correct distance to all PE pipe stubs inserted into electrofusion couplings. - Record of daily welding activities recorded. - Pipe and electrofusion coupling batch numbers to be recorded on daily weld log Record of weld type and location recorded on drawing for weld traceability | I | During setup and installation process | WP |  | V | Contractor’s Checklists, Daily Weld Record Sheet Photos |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |

|  |  |  |  |  |  |  | CONSTRUCTION VERIFICATION (Initial and Date) |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item No. | Inspection / Test Point | Responsibility | Specification Reference | Conformance Criteria | Method | Frequency | Contractor | Designer / IV / Client Rep. | Customer | Records or Checklist Reference |
| Construction (In-process) Inspections and Tests |  |  |  |  |  |  |  |  |  |  |
| 12. | Back fill pipe trench | CR | TWP-19-074-001 typical trench details and as noted | - Pipe embedment material cover of min 100mm 70% compaction required. - Embedment and backfill material shall be placed and compacted in 150mm thick layers to achieve CBR of 5% and final 95%R compaction results | I | As required per drawings and specification during back filling operations | HP |  | V | Photographs |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 13. | Hydrostatic pressure test of new water main | CR,S | WSAA 03 2011-3.1 CL 19.4 0001-STN-TW-DE-0004, AS2566.2 Appendix M | [INTERNAL HOLD POINT] - NATA Calibrated gauges- 2 of with a pressure rating of 1-2500 kpa with figure interval of 500 kpa and minor graduations of 50 kpa. - Gauges shall have a min dial face size of 50mm - Pipe to be filled with potable water and test pressure applied, bleed the residual air from the system via a bleed valve attached to the high point of the pipe line As per MRWA 19.4.1.1 PE Pipeline Testing | T | Prior to permanent reinstatement | HP | - | HP | Photos and MS Civil MSF250 pressure test record |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 14. | Final Inspection of site work | CR,S | IFC Drawings | [INTERNAL HOLD POINT] - 100% of works completed in accordance with IFC Drawings (or evidence of variation direction provided), Specifications and Work Package Environmental Management Plan All NCRs closed out. | R | Completion of works in the field | V | - | HP | Photographs |
| Remarks / NCR No. / RFI No: |  |  |  |  |  |  |  |  |  |  |
| 15. | As-constructed details recorded | CR,S |  | [INTERNAL HOLD POINT] As-constructed details recorded on the controlled mark-up drawings and/or digital format. | R | Each lot | V | - | HP | Redline Mark-up Drawings and supply of as-constructed data in accordance with the TasWater Asset Data Specification. |

| LEGEND |  |  |  |  |
| --- | --- | --- | --- | --- |
| RESPONSIBILITY |  |  | METHOD | VERIFICATION REQUIREMENT |
| Customer Team | Paneltec Team | Designer / Independent Verifier / Client Rep | I - Inspection | V - Verification |
| S - Supervisor | CR - Paneltec Group Representative | DR - Designer’s Representative | R - Review | M - Milestone |
| SE - Site Engineer | SV - Surveyor | GE - Geotechnical Engineer | S - Survey | HP - Hold Point |
| PE - Project Engineer |  | IV - Independent Verifier | T - Test | WP - Witness Point |
| PM - Project Manager |  | PR - Principal’s Representative |  |  |
| DM - Design Manager |  |  |  |  |
| EA - Environmental Advisor |  |  |  |  |
| QA - Quality Advisor |  |  |  |  |

QUALITY CONTROL CHECKLISTS (QCC)

PART 2 OF INSPECTION & TEST PLAN

Supplementary Quality Control Checklists (only if referenced in Part 1) to be detailed below and appended to Part 2:

| Part 1 Ref. # | QCC Document # | QCC Rev. # | QCC Document Title |
| --- | --- | --- | --- |

LOT VERIFICATION CHECKLIST (LVC)

PART 3 OF INSPECTION & TEST PLAN

| Lot Number: |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Lot Description: |  |  |  |  |  |  |  |
| Part 1 Ref No. | Item |  |  |  | No. of Records Required | Remarks (initial / date) |  |
| Quality Control Checklists / Records |  |  |  |  |  |  |  |
| 1 | Lot Traceability Map |  |  |  |  |  |  |
|  | Incoming Inspection Checklist |  |  |  |  |  |  |
|  | Delivery Dockets |  |  |  |  |  |  |
|  | Progress / Completion Photographs |  |  |  |  |  |  |
|  | Redline Mark-Up Drawing(s) |  |  |  |  |  |  |
| Survey Results |  |  |  |  |  |  |  |
|  | Compliance Survey Report |  |  |  |  |  |  |
| Test Results |  |  |  |  |  |  |  |
| Conformance of Work Statement (if required): The works for this construction lot conforms in respects with the standards and requirements specified for the Project. |  |  |  |  |  |  |  |
| Name: |  |  | Signed: | Paneltec Representative |  |  | Date: / /2023 |
| Name: |  |  | Signed: | Supervisor |  |  | Date: / /2023 |
| Conformance / Verification of Construction Lot Statement: This closed lot conforms in all respects with the standards and requirements specified in the Contract Documents. The lot verification records are complete and attached. Any non-conformances have been dispositioned in accordance with the contract requirements. |  |  |  |  |  |  |  |
| Name: |  |  | Signed: | Customer Project Manager / Project Engineer |  |  | Date: / /2023 |
| Independent Review (if required): |  |  |  |  |  |  |  |
| Name: |  |  | Signed: | Designer / IV / Client Representative |  |  | Date: / /2023 |
| Quality Review (if required): |  |  |  |  |  |  |  |
| Name: |  |  | Signed: | Quality Advisor |  |  | Date: / /2023 |