# Procedure

Management of Paneltec Pty Ltd will ensure that the use of electrical wiring, portable tools and extension leads will be in accordance with the provisions of Australian Standard AS-3000, Wiring Rules.

# Selection and Use General:

- Battery powered tools are to be used in the first preference.

- Correct tools should be chosen to suit a particular job.

- Properly designed and correctly insulated tools must be used.

- All tools and equipment must be in good order and regularly maintained.

- Only suitably trained persons will use electrical tools and equipment.

- Hand tools and leads should be checked for wear, breakages and damage before use.

- Tools found to be defective must immediately be withdrawn from service and labelled ‘DANGER - DO NOT USE’ (refer Lock Out & Tagging procedure) if the tool or equipment is to be repaired, or otherwise directly made inoperable and safely disposed of, or destroyed.

- Whilst on site any electrical equipment found without a tag of current date issued by a suitably qualified person will not be used.

- Only use heavy duty leads and do not extend leads to over 35m in length.

- All portable power outlets must be RCD protected. RCD to be tested daily by pressing test button and resetting on/off switch. A record of testing is to be maintained.

- RCD’s are to be used at all times when using portable electric power tools and leads.

- Piggy-back or portable domestic power adaptors are not to be used on site.

- Where practicable all electrical leads will be kept off the ground on insulated hangers or on insulated lead stands.

- All plugs and sockets will be non-wireable (moulded), or transparent.

- Electric leads and equipment must be kept away from water.

- Connections and disconnections of power leads shall not be made while the current is turned on.

- Generators to be fitted with a 30mA RCD. RCD to be tested daily by pressing test button and resetting on/off switch.

- No unauthorised person shall attempt to repair an electrical appliance- Report it to your supervisor.

# Extension sockets and plugs exposed to water

- Where flexible extension cords are linked together and used outdoors or where water may be present, the extension socket and plug should be protected by design or enclosure against the ingress of water.

# Testing & Tagging of plant, portable electrical equipment and appliances, and flexible electrical cords

- All plant including portable electrical equipment and flexible electrical cords, shall be visually inspected for wear and mechanical damage, and tested in accordance with AS/NZS 3760: 2010 (in service safety and inspection & testing of electrical equipment) for earth continuity, and insulation resistance by a competently trained qualified and experienced person.

- Inspection and testing should be undertaken prior to its first use, and every 3 calendar months thereafter, while being used in the construction & demolition fields as per Table 3 below from AS/NZS 3012-2010 (Electrical Installations Construction & Demolition Sites) and every 6 months in the workshop area (Table 4 of the AS/NZS 3760: 2010), for other electrical equipment see Table 4 of the AS/NZS 3760: 2010.

- All electrical equipment shall carry a current test tag.

- Tested portable electrical equipment and flexible electrical cords shall be tagged (preference on construction & demolition sites is to have tags colours as suggested in AS/NZS 3012-2010 Appendix F below) , and all test results shall be recorded, and records kept on site or made available for audit.

- The details recorded shall include the following:

  - date of inspection

  - plant number of the item inspected

  - licence number of the inspecting electrician

  - any repairs required as a result of the inspection.

Where electrical equipment is hired, management will ensure that the same requirements for Work Health and Safety as those required on site are specified to the Hire Company as a condition of the Hire Agreement.

# Records:

- An Electrical Equipment Register of all tagged items is to be maintained – this is usually supplied by the electrician or electrical tag company.

| PROCEDURE RECORDS |  |
| --- | --- |
| Number | Detail |
| - | Electrical Register to be maintained by electrical contractor. |
| SF-07 | Register of Approved Suppliers |